## CALCULO INS SOLAR
Loads | P.Unit | H | P. TOT | POW + MARG. | Data and Specifications
[5 empty] | Power in Wh/Day | 2807.0175 |  | Needed panels | 4
[5 empty] | Voltage Battery | 24 |  | Serial panel group | 1
Bulbs/Lamps | 0 | 10 | 0 | 0 | Autonomy (Days) | 3 |  | Parallel panel group | 4
Appliance 1 | 500 | 4 | 2000 | 2400 |  |  |  | Battery | 12030.0752 | W
Appliance 2 | 0 | 0 | 0 | 0 | P. Panel (in W) | 180 |  | Battery Capacity | 501.2531 | A/h
Appliance 3 | 0 | 3 | 0 | 0 | PSH - Kwh/m2 (According to Radiation data) | 5.4592 |  | Inverter Power (Oversized) | 2400 | W
Appliance 4 | 0 | 2 | 0 | 0 | Barcelona | 2
[5 empty] | Panel Voltage Max. | 36 |  | Panels | 3.174 | 4
Total | 500 | 19 | 2000 | 2400 | Imax. Panel | 4.9 |  | Serial | 0.66667 | 1
[5 empty] | Max. Seasonal Discharge Depth | 0.7 |  | Parallel | 4 | 4
Gadgets CC | 0 | 25 | 0 | 0 | Maximum Day Discharge Depth | 0.15
[5 empty] | I. Max. Panel In Shortcircuit | 5.3 |  | Ah | 116.9591
[5 empty] | POTENCIA en CC | 0 |  | Courrent Pnel | 21.4243
|  |  | P.TOT | 2807.0175 | POTENCIA en AC | 500 |  | Parallel panel group | 4.3723 | 5
[5 empty] | Global Work Factor | 0.9 |  | Nominal Capacity Battery Day | 18713.4503 | W/h | 779.7271 | Ah
Radiation Data base | [7 empty] | Nominal Capacity Battery Seasonal | 12030.0752 | W/h | 501.2531 | Ah
https://renovables.tulider.net/pv/hsp/ | [7 empty] | Input Regulatory Calculation | 33.125 | A
or: | [7 empty] | Output Regulatory Calculation | 27.4123 | A
Off-Grid Self-Consumption Installations | [7 empty] | Inverter Power (Oversized) | 2400 | W
CANAL DE YOUTUBE
https://www.youtube.com/c/EnergiaTecnologiayDemasVideos
|  |  | LUGAR |  | DATO1 | RADIACION MEDIA
|  |  | Manual data entry ----> |  | Manual data entry ----> | 2 | 1
|  |  | A Coruña |  | A Coruña | 4.7167 | 1
|  |  | Albacete |  | Albacete | 5.4592 | 1
|  |  | Algarve |  | Algarve | 5.9825 | 1
|  |  | Alenteio |  | Alenteio | 5.0325
|  |  | Alicante |  | Alicante | 5.78
|  |  | Almeria |  | Almeria | 6.0217
|  |  | Avila |  | Avila | 4.9433
|  |  | Badajoz |  | Badajoz | 5.725
|  |  | Barcelona |  | Barcelona | 5.4592
|  |  | Bilbao |  | Bilbao | 4.0883
|  |  | Burgos |  | Burgos | 4.7892
|  |  | Caceres |  | Caceres | 5.6642
|  |  | Cadiz |  | Cadiz | 5.9333
|  |  | Cantabria |  | Cantabria | 3.8217
|  |  | Castellon |  | Castellon | 5.63
|  |  | Ciudad Real |  | Ciudad Real | 5.5942
|  |  | Cordoba |  | Cordoba | 5.7317
|  |  | Cuenca |  | Cuenca | 5.315
|  |  | Faro |  | Faro | 6.085
|  |  | Gerona |  | Gerona | 5.2725
|  |  | Granada |  | Granada | 5.8692
|  |  | Granada |  | Granada | 5.8692
|  |  | Guadalajara |  | Guadalajara | 5.4983
|  |  | Huelva |  | Huelva | 5.975
|  |  | Huesca |  | Huesca | 5.595
|  |  | Ibiza |  | Ibiza | 5.8317
|  |  | Jaen |  | Jaen | 5.855
|  |  | Leon |  | Leon | 5.3542
|  |  | Lerida |  | Lerida | 5.4867
|  |  | Lerida |  | Lerida | 5.4867
|  |  | Lisboa |  | Lisboa | 5.445
|  |  | Lanzarote |  | Lanzarote | 6.2425
|  |  | Las Palmas |  | Las Palmas | 5.4767
|  |  | Logroño |  | Logroño | 4.7392
|  |  | Leon |  | Leon | 5.4042
|  |  | Lerida |  | Lerida | 5.29
|  |  | Lugo |  | Lugo | 4.495
|  |  | Madrid |  | Madrid | 5.6033
|  |  | Malaga |  | Malaga | 5.885
|  |  | Mallorca |  | Mallorca | 5.5892
|  |  | Menorca |  | Menorca | 5.7217
|  |  | Murcia |  | Murcia | 5.7425
|  |  | Orense |  | Orense | 4.9267
|  |  | oviedo |  | oviedo | 4.3483
|  |  | Palencia |  | Palencia | 5.1792
|  |  | Pamplona |  | Pamplona | 4.6808
|  |  | Pontevedra |  | Pontevedra | 5.0025
|  |  | Porto |  | Porto | 5.4117
|  |  | Salamanca |  | Salamanca | 5.3542
|  |  | Sevila |  | Sevila | 5.8742
|  |  | Soria |  | Soria | 5.2583
|  |  | Tarragona |  | Tarragona | 5.5433
|  |  | Tenerife |  | Tenerife | 6.2857
|  |  | Teruel |  | Teruel | 5.2867
|  |  | Toledo |  | Toledo | 5.5092
|  |  | Valencia |  | Valencia | 5.84
|  |  | Valladolid |  | Valladolid | 5.2308
|  |  | Vitoria |  | Vitoria | 4.4367
|  |  | Zamora |  | Zamora | 5.355
|  |  | Zaragoza |  | Zaragoza | 5.4625
Note on G12: ES el valor menor de la tabla de radiacion, (Hd)que corresponde en este caso a "Diciembre"
Note on H11: According to Radiation data online table
Note on H13: Max voltage according to panel specifications
Note on H14: Maximum current according to panel specifications.
Note on H15: Maximum seasonal discharge depth By default 0,70
Note on H16: Maximum Day discharge depth By default 0,15
Note on H17: Maximum current in short circuit conditions according to panel specifications
Note on H20: Default 0,90
Note on K6: Con MPPT
Note on K19: if we do not use an MPPT controller
Note on L19: if we do not use an MPPT controller